{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":19,"n_cols":6,"rows_kept":19,"merged":[[0,0,0,5],[18,0,18,5]]}
["自贡市中医医院\n全院区变压器预试预检清单\n（以实际为准）"]
["变压器","生产时间","数量","合计/KVA","区域","存在安全隐患问题"]
["10KV高压环网柜",null,"2台",null,"卧龙湖"]
["高压隔离柜",null,"3套",null,"卧龙湖"]
["高压开关柜",null,"13台",null,"卧龙湖"]
["消谐装置",null,"2套",null,"卧龙湖"]
["低压配电屏",null,"40台",null,"卧龙湖"]
["直流屏1套",null,"1台",null,"卧龙湖"]
["DTU终端柜",null,"1台",null,"卧龙湖"]
["室内干变1250KVA",null,"4台","5000KVA","卧龙湖"]
["室内干变1000KVA",null,"1台","1000KVA","卧龙湖"]
["室外美变 630KVA","2010-12-01","3台","1890KVA","马冲口","变压器及配电屏陈旧功率小不能满足发展使用，有安全隐患。"]
["室外欧变 630KVA","2013-11-01","1台","630KVA","马冲口","变压器及配电屏陈旧功率小不能满足发展使用，变压器自动开关已出现自动合闸失灵现象，有安全隐患。"]
["室外欧变 400KVA","2013-11-01","1台","400KVA","马冲口","变压器及配电屏陈旧功率小不能满足发展使用，有安全隐患。"]
["室外杆架试400KVA","2005-03-01","1台","400KVA","马冲口","变压器及配电屏陈旧功率小不能满足发展使用，有安全隐患。"]
["室外杆架试250KVA","2000-01-01","1台","250KVA","马冲口","变压器及配电屏陈旧功率小不能满足发展使用，有安全隐患。"]
["室外杆架试200KVA","2005-03-01","1台","200KVA","汇东","变压器及配电屏陈旧功率小不能满足正常使用，2024年8月变压器已出现超负荷B相发烫自燃。"]
["总数/合计",null,null,"9820KVA"]
["备注：检测所有变压器、低压配电屏、发电机配电屏、操作工具。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0}